## Input
Basic Traffic Analysis |  |  |  | Information Only
Contract Name: | <Enter Project Name>
Date: | 2026-07-29 20:21 | "User input at green cells only"
Letable Area in Sq.Metres | 3600
Building Population (Area per person) | 450 | 8 | Sq. Metres per person
Entrance Opening Width | 900
No of Cars | 2.25 | 200 | Persons per Lift
No of Passengers | 13 | .
No of Stops | 3
HQ = Travel / Metres | 12
V = Speed # m/min. | 60 | 1 | m/Sec
PASSENGERS PER TRIP | 10.4
TRIP LENGTH LOCAL ZONE | 12
AVERAGE TRIP LENGTH | 4.0599
AVERAGE TRIP TIME | 6.8705
TRIP TIME LOCAL ZONE | 20.3075
DOOR CLOSE TIME | 7.0938
PASSENGER TRANSFER TIME | 20.6728
LOST TIME | 2.7767
ROUND TRIP TIME (SECS) | 50.8508
PASS. HAND. CAP. IN 5 MINS. | 61.356
NUMBER OF CARS REQUIRED | 1.1001
ACTUAL NUMBER OF CARS | 2.25
AVERAGE WAITING INTERVAL (SECS) | 22.6003
THEORETICAL A. W. T. (SECS) | 12.4302
HANDLING CAPACITY IN 5 MINS (%) | 30.678
Good
ISO LOADS
320
400
450
550
630
800
900
1000
1150
1250
1350
1600
2000
2500
3000
3500
Please Note:
This traffic calculation is only to be used as basic
guideline. Schindler can offer you a more detailed
and comprehensive anaylsis if required.
View Data Sheet

## Data
TRAFFIC STUDY PASSENGER ELEVATORS
CONTRACT: | <Enter Project Name>
LETABLE AREA IN SQ. METRES : |  | 3600
BUILDING POPULATION : |  | 450 | USING SQUARE METRES PER PERSON OF : | [5 empty] | 8
15% OF POPULATION : |  | 67.5 | STOPS ABOVE OR BELOW LOBBY |  |  | 3 | LOC.ZONE TRAVEL (M): |  | 12
OPENING IN MM : |  | 900 | EXP/STOP (PE): | 0 |  |  | EXP.ZONE TRAVEL: |  | 0
NO/CARS: |  | 2.25 | NO. PASS | 13 |  |  | DATE: |  | 2026-07-29 20:21
SPEED OF LIFT (# meters per minute) |  | 60 | 90 | 105 | 120 | 150 | 180 | 210 | 240
R | NO. OF PASSENGERS | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
V | SPEED IN METRES PER SECOND | 1 | 1.5 | 1.75 | 2 | 2.5 | 3 | 3.5 | 4
N | NO. OF STOPS ABOVE LOBBY | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
R | PASSENGERS PER TRIP | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4
PL | NO. OF PROBABLE LOCAL STOPS | 2.9558 | 2.9558 | 2.9558 | 2.9558 | 2.9558 | 2.9558 | 2.9558 | 2.9558
PE | NO. OF PROBABLE EXPRESS STOPS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P | TOTAL PROBABLE STOPS | 2.9558 | 2.9558 | 2.9558 | 2.9558 | 2.9558 | 2.9558 | 2.9558 | 2.9558
SL | TRIP LENGTH LOCAL ZONE | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
SE | TRIP LENGTH EXPRESS ZONE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
J | AVERAGE TRIP LENGTH | 4.0599 | 4.0599 | 4.0599 | 4.0599 | 4.0599 | 4.0599 | 4.0599 | 4.0599
TJ | AVERAGE TRIP TIME | 6.8705 | 6.2342 | 6.1158 | 5.2363 | 5.2363 | 5.2363 | 5.2363 | 5.2363
TL | TRIP TIME LOCAL ZONE | 20.3075 | 18.4269 | 18.0768 | 15.4772 | 15.4772 | 15.4772 | 15.4772 | 15.4772
TAE | ADDITIONAL EXPRESS TIME | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TE | TRIP TIME EXPRESS ZONE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TD | DOOR CLOSE TIME | 7.0938 | 7.0938 | 7.0938 | 7.0938 | 7.0938 | 7.0938 | 7.0938 | 7.0938
TR | PASSENGER TRANSFER TIME | 20.6728 | 20.6728 | 20.6728 | 20.6728 | 20.6728 | 20.6728 | 20.6728 | 20.6728
TA | LOST TIME | 2.7767 | 2.7767 | 2.7767 | 2.7767 | 2.7767 | 2.7767 | 2.7767 | 2.7767
RTT | ROUND TRIP TIME (SECS) | 50.8508 | 48.9702 | 48.6201 | 46.0205 | 46.0205 | 46.0205 | 46.0205 | 46.0205
HC | PASS. HAND. CAP. IN 5 MINS. | 61.356 | 63.7123 | 64.1711 | 67.7959 | 67.7959 | 67.7959 | 67.7959 | 67.7959
NR | NUMBER OF CARS REQUIRED | 1.1001 | 1.0595 | 1.0519 | 0.99564 | 0.99564 | 0.99564 | 0.99564 | 0.99564
NO | ACTUAL NUMBER OF CARS | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25 | 2.25
AWI | AVERAGE WAITING INTERVAL (SECS) | 22.6003 | 21.7645 | 21.6089 | 20.4535 | 20.4535 | 20.4535 | 20.4535 | 20.4535
TAWT | THEORETICAL A. W. T. (SECS) | 12.4302 | 11.9705 | 11.8849 | 11.2494 | 11.2494 | 11.2494 | 11.2494 | 11.2494
QC | HANDLING CAPACITY IN 5 MINS (%) | 30.678 | 31.8561 | 32.0855 | 33.898 | 33.898 | 33.898 | 33.898 | 33.898
FT | BUILDING FILLING TIME (MINS) | 16.2983 | 15.6956 | 15.5833 | 14.7502 | 14.7502 | 14.7502 | 14.7502 | 14.7502
|  | 7.0938 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0
|  | 7.0938 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0
|  | 7.0938 | 0.95
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
|  | 0 | 0
Return to Input Page
Print Data Sheet